## YJLV English
0.6/1kV-1 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
1X10 | 0.7 | 1.4 | 8.04 | 75 | 3.08 | 55 | 71
1X16 | 0.7 | 1.4 | 9.04 | 106 | 1.91 | 71 | 91
1X25 | 0.9 | 1.4 | 10.59 | 150 | 1.2 | 94 | 115
1X35 | 0.9 | 1.4 | 11.59 | 180 | 0.868 | 115 | 140
1X50 | 1 | 1.4 | 13.09 | 240 | 0.641 | 140 | 165
1X70 | 1.1 | 1.4 | 14.99 | 320 | 0.443 | 180 | 205
1X95 | 1.1 | 1.5 | 16.775 | 400 | 0.32 | 220 | 245
1X120 | 1.2 | 1.5 | 18.375 | 500 | 0.253 | 260 | 280
1X150 | 1.4 | 1.6 | 20.51 | 600 | 0.206 | 300 | 315
1X185 | 1.6 | 1.6 | 22.61 | 730 | 0.164 | 350 | 360
1X240 | 1.7 | 1.7 | 25.195 | 930 | 0.125 | 414 | 420
1x300 | 1.8 | 1.8 | 27.83 | 1140 | 0.1 | 485 | 475
1x400 | 2 | 1.9 | 31.415 | 1500 | 0.0778 | 570 | 545
1x500 | 2.2 | 2 | 34.9 | 1800 | 0.0605 | 670 | 620
1X630 | 2.4 | 2.2 | 39.07 | 2285 | 0.0469 | 790 | 705
0.6/1kV-2 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
2X10 | 0.7 | 1.8 | 15.375 | 200 | 3.08 | 58 | 78
2X16 | 0.7 | 1.8 | 17.375 | 270 | 1.91 | 75 | 100
2X25 | 0.9 | 1.8 | 20.475 | 380 | 1.2 | 100 | 130
2X35 | 0.9 | 1.8 | 22.475 | 480 | 0.868 | 120 | 155
2X50 | 1 | 1.8 | 20.275 | 490 | 0.641 | 150 | 185
2X70 | 1.1 | 1.8 | 23.275 | 630 | 0.443 | 190 | 225
2X95 | 1.1 | 1.9 | 26.16 | 820 | 0.32 | 235 | 275
2X120 | 1.2 | 2 | 29.35 | 1000 | 0.253 | 275 | 315
2X150 | 1.4 | 2.2 | 32.62 | 1250 | 0.206 | 315 | 350
2X185 | 1.6 | 2.3 | 36.005 | 1540 | 0.164 | 365 | 395
0.6/1kV-3 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
3X10 | 0.7 | 1.8 | 17.2266 | 250 | 3.08 | 50 | 66
3X16 | 0.7 | 1.8 | 19.3806 | 330 | 1.91 | 65 | 85
3X25 | 0.9 | 1.8 | 22.827 | 480 | 1.2 | 87 | 110
3X35 | 0.9 | 1.8 | 24.981 | 580 | 0.868 | 105 | 130
3X50 | 1 | 1.8 | 24.374 | 670 | 0.641 | 130 | 160
3X70 | 1.1 | 1.9 | 29.355 | 910 | 0.443 | 165 | 195
3X95 | 1.1 | 2 | 33.564 | 1170 | 0.32 | 205 | 235
3X120 | 1.2 | 2.1 | 35.874 | 1460 | 0.253 | 240 | 265
3X150 | 1.4 | 2.3 | 39.861 | 1820 | 0.206 | 270 | 300
3X185 | 1.6 | 2.4 | 44.07 | 2200 | 0.164 | 315 | 340
3X240 | 1.7 | 2.6 | 51.062 | 2850 | 0.125 | 375 | 395
3X300 | 1.8 | 2.7 | 56.104 | 3500 | 0.1 | 435 | 445
3X400 | 2 | 3 | 62.412 | 4500 | 0.0778 | 510 | 510
0.6/1kV-4 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
4X10 | 0.7 | 1.8 | 18.6306 | 300 | 3.08 | 50 | 66
4X16 | 0.7 | 1.8 | 21.0446 | 400 | 1.91 | 65 | 85
4X25 | 0.9 | 1.8 | 24.907 | 570 | 1.2 | 87 | 110
4X35 | 0.9 | 1.8 | 28.321 | 710 | 0.868 | 105 | 130
4X50 | 1 | 1.8 | 28.375 | 850 | 0.641 | 130 | 160
4X70 | 1.1 | 2 | 33.14 | 1160 | 0.443 | 165 | 195
4X95 | 1.1 | 2.1 | 37.08 | 1520 | 0.32 | 205 | 235
4X120 | 1.2 | 2.2 | 40.8 | 1898 | 0.253 | 240 | 265
4X150 | 1.4 | 2.4 | 45.16 | 2369 | 0.206 | 270 | 300
4X185 | 1.6 | 2.6 | 52.13 | 2925 | 0.164 | 315 | 340
4X240 | 1.7 | 2.8 | 57.81 | 3700 | 0.125 | 375 | 395
4X300 | 1.8 | 3 | 63.49 | 4580 | 0.1 | 435 | 445
4X400 | 2 | 3.3 | 70.91 | 5800 | 0.0778 | 510 | 510
0.6/1kV-5 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
5X10 | 0.7 | 1.8 | 18.8 | 360 | 3.08 | 50 | 66
5X16 | 0.7 | 1.8 | 21.8 | 485 | 1.91 | 65 | 85
5X25 | 0.9 | 1.8 | 26.2 | 690 | 1.2 | 87 | 110
5X35 | 0.9 | 1.8 | 28 | 865 | 0.868 | 105 | 130
5X50 | 1 | 1.9 | 32.368 | 1138 | 0.641 | 130 | 160
5X70 | 1.1 | 2.1 | 37.366 | 1575 | 0.443 | 165 | 195
5X95 | 1.1 | 2.2 | 41.68 | 2068 | 0.32 | 205 | 235
5X120 | 1.2 | 2.4 | 46.194 | 2550 | 0.253 | 240 | 265
5X150 | 1.4 | 2.6 | 53.142 | 3165 | 0.206 | 270 | 300
5X185 | 1.6 | 2.8 | 58.866 | 3950 | 0.164 | 315 | 340
5X240 | 1.7 | 3 | 65.558 | 5025 | 0.125 | 375 | 395
5X300 | 1.8 | 3.2 | 72.008 | 6190 | 0.1 | 435 | 445
0.6/1kV-3+1 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
3X16+1X10 | 0.7/0.7 | 1.8 | 19.4125 | 370 | 1.91/3.08 | 65 | 85
3X25+1X16 | 0.9/0.7 | 1.8 | 22.8222 | 520 | 1.20/1.91 | 87 | 110
3X35+1X16 | 0.9/0.7 | 1.8 | 25.1327 | 650 | 0.868/1.91 | 105 | 130
3X50+1X25 | 1.0/0.9 | 1.8 | 28.218 | 780 | 0.641/1.20 | 130 | 160
3X70+1X35 | 1.1/0.9 | 1.9 | 31.868 | 1050 | 0.443/0.868 | 165 | 195
3X95+1X50 | 1.1/1.0 | 2.1 | 35.703 | 1460 | 0.320/0.641 | 205 | 235
3X120+1X70 | 1.2/1.1 | 2.2 | 39.584 | 1820 | 0.253/0.443 | 240 | 265
3X150+1X70 | 1.4/1.1 | 2.3 | 43.5805 | 2150 | 0.206/0.443 | 270 | 300
3X185+1X95 | 1.6/1.1 | 2.5 | 49.7705 | 2725 | 0.164/0.320 | 315 | 340
3X240+1X120 | 1.7/1.2 | 2.7 | 55.2685 | 3480 | 0.125/0.253 | 375 | 395
3X300+1X150 | 1.8/1.4 | 2.9 | 57 | 4230 | 0.100/0.206 | 435 | 445
3X400+1X185 | 2.0/1.7 | 3.1 | 70 | 5520 | 0.0778/0.164 | 510 | 510
0.6/1kV-4+1 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
4X16+1X10 | 0.7/0.7 | 1.8 | 21.2908 | 450 | 1.91/3.08 | 65 | 85
4X25+1X16 | 0.9/0.7 | 1.8 | 25.6788 | 650 | 1.20/1.91 | 87 | 110
4X35+1X16 | 0.9/0.7 | 1.8 | 28.2438 | 795 | 0.868/1.91 | 105 | 130
4X50+1X25 | 1.0/0.9 | 1.9 | 28.855 | 1020 | 0.641/1.20 | 130 | 160
4X70+1X35 | 1.1/0.9 | 2 | 32.24 | 1360 | 0.443/0.868 | 165 | 195
4X95+1X50 | 1.1/1.0 | 2.2 | 36.92 | 1870 | 0.320/0.641 | 205 | 235
4X120+1X70 | 1.2/1.1 | 2.3 | 40.815 | 2342 | 0.253/0.443 | 240 | 265
4X150+1X70 | 1.4/1.1 | 2.5 | 44.685 | 2778 | 0.206/0.443 | 270 | 300
4X185+1X95 | 1.6/1.1 | 2.7 | 50.655 | 3495 | 0.164/0.320 | 315 | 340
4X240+1X120 | 1.7/1.2 | 2.9 | 56.435 | 4416 | 0.125/0.253 | 375 | 395
4X300+1X150 | 1.8/1.4 | 3.1 | 64.025 | 5422 | 0.100/0.206 | 435 | 445
0.6/1kV-3+2 core aluminum conductor XLPE insulated PVC sheathed power cable
No. of cores and nominal cross section | Thickness of Insulation | Thickness of Sheath | Approx. overall Diameter | Approx. weight | Max. DC resistance of conductor（20℃） | Current carrying capacity
(mm2) | (mm) | (mm) | (mm) | (kg/km) | (Ω/km) | In Air(A) | In Ground(A)
3X16+2X10 | 0.7/0.7 | 1.8 | 20.7616 | 425 | 1.91/3.08 | 65 | 85
3X25+2X16 | 0.9/0.7 | 1.8 | 25.1766 | 600 | 1.20/1.91 | 87 | 110
3X35+2X16 | 0.9/0.7 | 1.8 | 26.7966 | 720 | 0.868/1.91 | 105 | 130
3X50+2X25 | 1.0/0.9 | 1.9 | 28.67 | 955 | 0.641/1.20 | 130 | 160
3X70+2X35 | 1.1/0.9 | 2 | 33.7 | 1230 | 0.443/0.868 | 165 | 195
3X95+2X50 | 1.1/1.0 | 2.2 | 38.3 | 1706 | 0.320/0.641 | 205 | 235
3X120+2X70 | 1.2/1.1 | 2.3 | 43.2 | 2180 | 0.253/0.443 | 240 | 265
3X150+2X70 | 1.4/1.1 | 2.4 | 46.5 | 2525 | 0.206/0.443 | 270 | 300
3X185+2X95 | 1.6/1.1 | 2.6 | 51.9 | 3195 | 0.164/0.320 | 315 | 340
3X240+2X120 | 1.7/1.2 | 2.8 | 58 | 4050 | 0.125/0.253 | 375 | 395
3X300+2X150 | 1.8/1.4 | 3 | 64.2 | 4983 | 0.100/0.206 | 435 | 445